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[bookmark: ADDENDUM_No._1]ADDENDUM #1
RFB #26-0074
ADULT DETENTION FACILITY BUILDING AUTOMATION SYSTEM REPLACEMENT

October 30, 2026

The following is to ensure that vendors have complete information prior to submitting a Request for Bid. Here are some clarifications regarding the Adult Detention Facility Building Automation System Replacement

Questions and/or statements of clarification are in bold font, and answers to specific questions are italicized.

Firms interested in submitting a Request for Bid must respond with complete information and deliver on or before 1:45 pm Tuesday, November 10,  2026. Late responses will not be accepted and will not receive consideration for final award.
“PLEASE ACKNOWLEDGE RECEIPT OF THIS ADDENDUM ON THE RFB RESPONSE PAGE.”
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Lee Barrier, NIGP-CPP
Senior Purchasing Agent




LB/ks

Addendum #1, RFB #26-0074

GENERAL:
· Bid Form - Reference new Bid Form.
· (Base Bid):
Description: For air handler units 5, 6, 7, 8, 9, 10, 11, 12, 17, 18, 19, 20, 21, 22, 23, 24, & 25 provide a pre-heat coil in the AHU. Include the labor, associated piping, piping specialties, ductwork, electrical, and pre-heat coil control valve for each unit for a complete installation. DDC controller, associated sensors, and other valves are to be part of the BAS Provider / Temperature Controls Contractor Alternate.
· Does the County have a project timeline established?
· No. The building is to remain functional throughout the project. The Contractor is to identify the number of days to complete the project.
· Will the County be holding any interviews with the vendors or contractors?
· No.
· Is there any prevailing wage requirements?
· No.
· What is to be included in the base bid v. alternate 1?
· Reference revised Bid Form. Base Bid is to be the installation of the multizone AHU pre-heat coils.
· Specification 01 23 00 Alternates
· Revise Alternate No. 2 to Not Applicable. (Reference revised Bid Form description above)


MECHANICAL:
· Are there existing raceways or cable trays above ceiling grids throughout the entire building? Will the Contractor need to provide if not?
· There are cable trays within the building but the BAS control wiring is to be routed separately from other data systems. Wiring to be installed per Division 26 and per the Building Data Communication Cabling requirements in the Invitation for Bids.
· Does all wire need to be in conduit, or are there only certain areas that will?
· Wiring to be installed per Division 26 and per the Building Data Communication Cabling requirements in the Invitation for Bids.
· If only 1 IP address is given, are there any particular switches that are required to be used?
· The County will determine which switch is to be used.
· Does the controls vendor need to provide test and balance?
· The Mechanical Contractor is to provide test and balance.
· Who has been doing the maintenance on the fire sprinkler system?
· Heritage Fire Protection, Inc.
· What refrigerant is in the chillers?
· South chillers are R-11. North chillers are R22.
· Specification 23 25 00 Water Treatment

· Water treatment is to be provided by Chemtreat. Contact: Darren Eskridge, darrene@chemtreat.com, 316-841-6252. Treatment of the heating water system is to be included in the Base Bid.
· The chilled and heating water systems will need to be tested prior to work commencing to determine existing treatment levels. The chilled system treatment will need to be updated after installation of new valves and strainers being cleaned. The heating water system is to be cleaned and flushed out after piping modifications, adding new valves and cleaning strainers. The heating system is estimated to be 15,000 gallons, but should be verified by the Contractor.
· Fire Alarm Modification
· CO detection for the boiler rooms is to be added to the existing fire alarm system. The system is JCI / Simplex. Contact: Doug Boudreau, douglas.boudreau@jci.com, 316-686-6363. Modifications to the fire alarm are to be included in the Base Bid.
· CO sensor to be equal to a Simplex TrueAlarm CO sensor base with sounder. Sensor is to be for use with 4007ES, and 4010ES or 4100ES fire alarm control units (FACU’s) with software revisions 2.01.02 or higher. Sensors to be set for OSHA compliancce of 30 ppm. Provide adequate number of sensors for room coverage.
· South Boiler Room (B030):
Add CO detection in the South Boiler room. E.C. to provide boxes, conduit, and pull wire (1- 18/2 FPLP and 1-14/2 FPLP) back to the FACU in B029. CO detector(s) to be added to the Idnet channel M1 from this panel. CO detector(s) are to be programmed and added to the graphics on the Truesite Workstation computer in Master Control. Temporal 4 notifications to be done with programming.
· North Boiler Room (B074):
Add CO detection in the North Boiler room. E.c. to provide boxes, conduit, and pull wire (1- 18/2 FPLP and 1-14/2 FPLP) back to the FACU in the North Housing 1st Floor Mezzanine. CO detector(s) to be added to the Idnet channel M4 from this panel. CO detector(s) to be programmed and added to the graphics on the Truesite Workstation computer in Master Control. Temporal 4 notifications to be done with programming.
· The existing Simplex 4020 panel serving the North end is to be replaced/upgraded to a 4100es panel. All cards in the panel are to be replaced and the programing upgraded to a newer revision that supports CO detection. The E.C. is to rework the 120V power to the new location. Existing 4100 cans in the area can be used.
· Inspection is to be scheduled and performed with the City of Wichita.


BID FORM
BID PROVIDED BY:

(Company Name)

I have received the Bid Documents, Specifications, and Construction Documents, collectively known as the Contract Documents for Construction of the

Adult Detention Facility Building Automation System Replacement
COUNTY BID NUMBER: 26-0074

as prepared by the Architect: Justin Graham, AIA, Associate Architect
Schaefer Architecture 257 N. Broadway
Wichita, Kansas 67202-2303
Telephone: (316) 684-0171
In submitting this Bid, I agree:

1. To hold my Bid open for 60 days after the date of this Bid.

2. To enter into and execute a Contract, if awarded on the basis of this Bid, and to proceed in accordance with the requirements of the General Conditions and Contract Form.
3. To provide all labor, materials, equipment, tools of trades and labor, accessories, appliances, warranties and guarantees, and to pay all royalties, fees, permits, licenses and applicable taxes necessary to complete the work in accordance with the proposed Contract Documents.
4. To remove and haul away from the construction site any and all debris arising from this contract and to assume sole liability for all removal, handling, and dumping of debris.

5. To comply with any and all local, state, federal or other governmental laws, rules and regulations with respect to the transportation, disposal, and dumping of debris and other excavated materials and Contractor shall secure any and all necessary permits and approvals incident to said transportation, dumping and disposal.
6. To further agree to indemnify and hold the Owner and Designer harmless from any and all claims
and/or damage of any kind whatsoever as a result of the Contractor’s performance of this Contract.

7. That attached to this Bid is one copy of the Certificate of Insurance including Contractor’s General Automotive Liability, Workers Compensation Insurance and Owner’s Liability Insurance.
8. CALENDAR DAYS:
The Undersigned agrees to reach substantial completion of the Work in 	 consecutive calendar days from the date of Notice to Proceed.
The Undersigned agrees to reach final completion of the Work in 	consecutive calendar days from the date of Substantial Completion.

Total Calendar Days 	


9. BID:
BASE BID
To complete the Base Bid Work, in the time stipulated, in accordance with the Bidding Documents as follows:

The Prime Contractor is to be a licensed General Contractor or licensed Mechanical Contractor.

Base Bid is to include items included in the Plans and Specifications (add additional descriptors and project requirements).





	Dollars ($	).

ALTERNATES:


Alternate 1: BAS Provider / Temperature Controls Contractor.
1. Building Controls and Services - Siemens Cost: $	
2. C&C Group – Schneider Electric Cost: $	
3. Dynamic Control Systems – Automated Logic Cost: 	
4. Five Star Mechanical – Reliable Controls Cost: $	
5. Johnson Controls Cost: $	
6. Sandifer Engineering & Controls, - Schneider Electric Cost:
$	
7. The Trane Co. – Trane Controls Cost: $	 Alternate 2: ( Not applicable)

Alternate 3: Chilled Water Pump VFD’s / BAS.
Description: Provide variable frequency drives for the chilled water pumps as noted on the Plans. Differential pressure sensors, flow meters, control valves and electrical changes are to be included for a complete installation.
1. Building Controls and Services - Siemens Cost: $	
2. C&C Group – Schneider Electric Cost: $	

3. Dynamic Control Systems – Automated Logic Cost: 
$	
4. Five Star Mechanical – Reliable Controls Cost: $	
5. Johnson Controls Cost: $	
6. Sandifer Engineering & Controls, - Schneider Electric Cost:
$	
7. The Trane Co. – Trane Controls Cost: $	
Alternate 4: Heating Water Pump VFD’s / BAS.
Description: Provide variable frequency drives for the heating water pumps as noted on the Plans. Differential pressure sensors and electrical are to be included for a complete installation.
1. Building Controls and Services - Siemens Cost: $	
2. C&C Group – Schneider Electric Cost: $	
3. Dynamic Control Systems – Automated Logic Cost:
$	
4. Five Star Mechanical – Reliable Controls Cost: $	
5. Johnson Controls Cost: $	
6. Sandifer Engineering & Controls, - Schneider Electric Cost:
$	
7. The Trane Co. – Trane Controls Cost: $	

Alternate 5: Airflow Measuring Stations / BAS.
Description: Replace the existing airflow measuring stations as noted on the controls schematics. Include removal of the old airflow measuring stations, patching the associated ductwork, and electrical for a complete installation.
1. Building Controls and Services - Siemens Cost: $	
2. C&C Group – Schneider Electric Cost: $	
3. Dynamic Control Systems – Automated Logic Cost:
$	

4. Five Star Mechanical – Reliable Controls Cost: $	
5. Johnson Controls Cost: $	
6. Sandifer Engineering & Controls, - Schneider Electric Cost:
$	
7. The Trane Co. – Trane Controls Cost: $	

10. ADDENDA:
The Bidder acknowledges receipt of the following numbered Addenda: None ( ) #1(	) #2(	) #3 (	) #4(	) #5(	)
11. AGREEMENTS:
The Undersigned agrees to the following terms and conditions:
a. An incomplete Bid, or other information not requested which is written on this Bid Form, may be cause for rejection.
b. Read the Invitation for Bids and the Instructions to Bidders carefully.
c. The Owner reserves the right to reject any or all Bids and to waive all technicalities should such action be deemed to be in the best interest of the Owner.
d. This Bid may not be withdrawn for a period of 60 calendar days following the receipt and opening.
e. Failure to acknowledge receipt of any Addendum issued may be cause for Bid rejection.
f. In the event that changes to the work are required, the undersigned agrees that ten percent (10% for Self-Perform, 5% for Sub, 3% for Sub of Sub) total between General and Subcontractors of his net costs shall be added thereto for Overhead, Profit and General Requirements (including but not limited to, Insurance and Bonds). Markup shall not be stacked; the Owner shall pay only the single percentage applicable to the tier actually performing the Work. 

12. MAJOR SUBCONTRACTORS:
The Undersigned acknowledges the following named major subcontractors are to be used for their respective division of work. Contractors shall identify by type, any disadvantaged, minority and women-owned businesses used as a subcontractor for this project.

Subcontractor:	 Address – City, State, Zip: 	 
Additional, if necessary:

13. DECLARATIONS:
The Undersigned hereby declares he has carefully examined the Drawings and Specifications, has visited the actual location of the work, has satisfied himself as to all conditions and understands that, in signing this Bid Form, he waives all right to plead any misunderstandings regarding same and agrees to be bound by the provisions of said Drawings and Specifications and all statements made therein.

The Undersigned proposes to enter into Contract and to furnish and pay for the specified Bonds and other required Documents within 10 working days after notification of award of Contract.

14. FIRM IDENTIFYING INFORMATION:
FIRM NAME 						 CONTACT 						 SIGNATURE 		TITLE 				 PRINT NAME 						 ADDRESS 	CITY/STATE 			ZIP 	 PHONE 	FAX 			HOURS 	 COMPANY WEBSITE ADDRESS 			E-MAIL 			 NUMBER OF LOCATIONS 	NUMBER OF PERSONS EMPLOYED		 TYPE OF ORGANIZATION:
Public Corporation   Private Corporation  Sole Proprietorship   Partnership   Small Business    General Nature of Business 	 Manufacturer   Distributor   Retail   Dealer  Service    
	Not Minority/Caucasian (00) publicly traded companies and nonprofits are in this category Minority Owned Business:
	African American (05), 	Asian Pacific (10), 	Subcontinent Asian (15), 	Hispanic (20),
	Native American (25), 	Other (30) - Please specify	,
	Not Minority/Caucasian – Woman Owned (50), 	African American – Woman Owned (55),
	Asian Pacific – Woman Owned (60), 	Subcontinent Asian – Woman Owned (65), 	Hispanic –
Woman Owned (70), 	Native American – Woman Owned (75), 	Other – Woman Owned (80)

Insurance registered in the State of Kansas with a minimum best rating of A-VIII: 	Yes 	No

15. SIGNATURE AND SEAL:
DATED THIS 	 DAY OF 	, 2024.


LEGAL NAME OF PERSON, FIRM OR CORPORATION

   MAILING ADDRESS OF ABOVE

SIGNATURE

TELEPHONE NUMBER	FAX NUMBER

(Affix Corporate Seal here)	E-MAIL
BID FORM
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